## NON CRITICAL SERVER ROOM
PRIORITY |  |  | LEGACY MINIMUM | UHS IT STANDARD
| GENERAL | DATE / TIME |  |  | DATE AND TIME
|  | INSPECTOR NAME |  |  | #
|  | CAMPUS |  |  | CLEAR LAKE | DOWNTOWN | MAIN | VICTORIA
|  | BUILDING |  |  | TEXT
|  | ROOM NUMBER |  |  | TEXT
HIGH |  | TEMPERATURE | 60 - 75F | 60 - 75F | #
HIGH |  | HUMIDITY | 30 - 50% RH | 30 - 50% RH | #
HIGH |  | ASSET TAG ON DOOR FRAME | YES | YES | # | NONE
MED |  | CONTROLLABLE THERMOSTAT | YES | YES | YES | NOT CONTROLLABLE | NONE IN ROOM
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | ROOM INFORMATION | ROOM TYPE | SHARED MOSTLY IT | DEDICATED | DEDICATED | SHARED MOSTLY IT | SHARED MOSTLY OTHERS
HIGH |  | ACCESS | READER OR IT MASTER KEY | READER W/ IT MASTER KEY | CARD READER | IT MASTER KEYED | COMMON KEYED | NONE
HIGH |  | CAMERA INTERIOR | YES | YES | YES | NO |  | NON OPERATIONAL
CS |  | CAMERA EXTERIOR | YES OR NOT REQUIRED | YES OR NOT REQUIRED | YES | NO | NOT REQUIRED | NON OPERATIONAL
HIGH |  | DOOR TYPE | SOLID | SOLID | SOLID | LOUVERED | GLASS
MED |  | ROOM LABEL | YES | YES | YES | NO
MED |  | DOOR SWING | DOES NOT AFFECT ROOM USE | OUT | OUT | IN | AFFECTS ROOM USE
HIGH |  | LIGHTING | OPERATIONAL | SWITCH | SWITCH | MOTION | NONE | SWITCH NON OPERATIONAL | MOTION NON OPERATIONAL
HIGH |  | WALLS TO DECK | YES | YES | YES | NO
LOW |  | CEILING | ANY | OPEN/NONE | OPEN/NONE | SHEETROCK | CEILING TILE
MED |  | FIRE SUPPRESSION | CLEAN AGENT | CLEAN AGENT | BUILDING STANDARD | PRE-ACTION | CLEAN AGENT | NONE (EXTIGUISHER REQ)
LOW |  | SPRINKLER HEADS | CAGED | CAGED | CAGED | NOT CAGED | NONE
HIGH |  | INSPECTED FIRE EXTINGUISHER | IF NO FIRE SUPPRESSION | NOT REQUIRED | NOT REQUIRED | CO2 OR CLEAN AGENT | WET TYPE (REPLACE) | INSPECTION REQUIRED
HIGH |  | SPACE FOR GROWTH | YES | YES | YES | NO
HIGH |  | POWER CORD TRIPPING HAZARD | NO | NO | NO | YES
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | HOUSE KEEPING | TRASH IN ROOM | NO | NO | NO | YES, REMOVE
LOW |  | FLOOR IS CLEAN | YES | YES | NO | YES, CLEANING REQUIRED
LOW |  | EQUIPMENT DUST FREE | YES | YES | NO | YES, CHECK ROOM PRESSURE
MED |  | INAPROPRIATE STORAGE | NO | NO | NO | YES
HIGH |  | ABANDONED CABLING | NO | NO | NO | YES
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | NON SERVICING SYSTEMS | WATER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | SEWER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | FIRE MAIN | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ROOF DRAINS | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ELECTRICAL PANELS | NO OR SERVICES ROOM | NO | NO | YES, SERVICES ROOM | YES, NOT APPROVED BY IT
HIGH |  | ACCESS CONTROL PANELS | NO OR IF APPROVED BY IT | NO OR IF APPROVED BY IT | NO | YES, APPROVED BY IT | YES, NOT APPROVED BY IT
HIGH |  | AV SYSTEMS | NO OR YES, APPROVED BY IT | NO OR IF APPROVED BY IT | NO | YES, APPROVED BY IT | YES, NOT APPROVED BY IT
|  |  | LEGACY MINIMUM | UHS IT STANDARD
MED | ROOM CABLE SUPPORT | OVERHEAD CABLE SUPPORT | ANY (NOT NONE) | BASKET OR LADDER | BASKET | LADDER | HOOKS | NONE, SUPPORT REQUIRED
MED |  | WALL CABLE SUPPORT | ANY (NOT NONE) | LADDER | BASKET | LADDER | D-RINGS | NONE, SUPPORT REQUIRED
MED |  | SUPPORT CAPACITY | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | TRAY FULL | REWORK REQUIRED
LOW |  | CABLE TRAY DRESSING | NEAT AND TIDY | NEAT AND TIDY | NEAT AND TIDY | REDRESSING REQUIRED
HIGH |  | HORIZONTAL PENETRATIONS | COMPLIANT OR SEALED | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | HORZ. PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | VERTICAL PENETRATIONS | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | NOT APPLICABLE
MED |  | VERTL PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | INCOMMING OSP CONDUIT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | OSP CONDUIT SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
MED |  | RAISED FLOOR | YES OR NONE | YES OR NONE | NO | YES, IN GOOD CONDITION | YES, MISSING TILES
HIGH |  | UNDER FLOOR CAPACITY | SPARE CAPACITY OR NA | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| MEP | LIGHTS | EMERGENCY OR HOUSE | EMERGENCY OR HOUSE | EMERGENCY | HOUSE POWER | NOT SUFFICIENT | UNKNOWN SUFFICIENT
|  | HVAC | DEDICATED | DEDICATED | DEDICATED | BUILDING AIR | NONE | UNKNOWN
|  | HVAC TYPE | ANY | ANY | CHILLED WATER | DX | BOTH | UNKNOWN
|  | WALL POWER | EMERGENCY OR HOUSE | EMERGENCY OR HOUSE | EMERGENCY | HOUSE POWER | NONE | UNKNOWN
MED |  | RACK CIRCUIT 1 -TWIST LOCK | EMERGENCY OR HOUSE | EMERGENCY | EMERGENCY | HOUSE POWER | NONE
MED |  | RACK CIRCUIT 2 -TWIST LOCK | EMERGENCY OR HOUSE | EMERGENCY OR HOUSE | EMERGENCY | HOUSE POWER | NONE
MED |  | RACK CIRCUIT 1 - NON LOCKING | EMERGENCY OR HOUSE | EMERGENCY | EMERGENCY | HOUSE POWER | NONE
MED |  | RACK CIRCUIT 2 - NON LOCKING | EMERGENCY OR HOUSE | EMERGENCY OR HOUSE | EMERGENCY | HOUSE POWER | NONE
MED |  | POSITIVE PRESSURE | YES | YES | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | GROUNDING AND BONDING | BUSS BAR | YES | YES | YES | NO
HIGH |  | TWO HOLE TUGS USED | YES | YES | YES | NO
HIGH |  | TRAY BONDED TO TGB | YES | YES | YES | NO
HIGH |  | RACK BONDED TO TGB | YES | YES | YES | NO
HIGH |  | UPS BONDED TO RACK | YES | YES | YES | NO
HIGH |  | PDU(S) BONDED TO RACK | YES | YES | YES | NO | NA
HIGH |  | OSP CABLE EQUIPMENT | YES | YES | YES | NO | NA
HIGH |  | RAISE FLOOR | YES | YES | YES | NO | NA
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| RACK RELATED | NUMBER OF RACKS / CABINETS |  |  | #
|  | RACK/CAB 1 SPARE RACK UNITS |  |  | #
|  | RACK/CAB 2 SPARE RACK UNITS |  |  | #
|  | RACK/CAB 3 SPARE RACK UNITS |  |  | #
|  | RACK/CAB 4 SPARE RACK UNITS |  |  | #
|  | SPARE PATCH PANEL PORTS |  |  | # | #
LOW |  | VERTICAL MANAGERS | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | REDRESSING REQUIRED | FULL | NONE
LOW |  | HORIZONTAL MANAGERS | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | REDRESSING REQUIRED | FULL | NONE
HIGH |  | FRONT CLEARANCE | NOT UNSAFE | 3FT+ | 3FT+ | 2FT+ | NONE | UNSAFE
HIGH |  | REAR CLEARANCE | NOT UNSAFE | 3FT+ | 3FT+ | 2FT+ | NONE | UNSAFE
LOW |  | ROOM FOR ADD'L RACK/CABINET | ANY | YES | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| UPS | UPS TYPE | IN CABINET OR CENTRALIZED | IN CABINET OR CENTRALIZED | IN CABINET | CENTRALIZED | NONE
HIGH |  | UPS STATUS | PASSED TEST | PASSED TEST | PASSED TEST | FAILS TEST | NONE
MED |  | UPS MONITORED | ANY | ANY | YES | NO
MED |  | ROOM TEMP MONITORING | ANY | ANY | YES | NO | YES, BUT NOT VIA UPS
MED |  | SPARE CAPACITY | YES | YES | YES | NO | NA
MED |  | STEP DOWN TRANSFORMER | ANY | N/A | YES | NO | NA
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | LABELING | ROOM | YES | YES | YES | NO
LOW |  | RACKS/CABINETS | YES | YES | YES | NO
LOW |  | FIBER CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | FIBER PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BACKBONE COPPER CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BACKBONE COPPER PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | HORIZONTAL CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | HORIZONTAL PATCH PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | SWITCHES | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | UPS | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BUSS BAR | YES | YES | YES | NO | UPDATE REQUIRED
HIGH |  | FIRE STOP ASSEMBLIES | YES | YES | YES | NO | UPDATE REQUIRED
MED |  | SERVERS AND OTHER APPLIANCES | YES | YES | YES | NO | UPDATE REQUIRED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| BACKBONE | FIBER CABLE MFG | ANY | ANY | COMMSCOPE | CORNING | PYRSMIAN | DRAKA | OTHER
|  | FIBER CONNECTIVITY | ANY | ANY | LC | ST | APC | SC | COMBINATION
MED |  | FIBER AT CAPACITY | NO | NO | YES | NO
|  | BACKBONE COPPER CABLE | ANY | ANY | 25 PAIR | 50 PAIR | 100 PAIR | NONE
MED |  | COPPER BACKBONE AT CAPACITY | NO OR N/A | NO OR N/A | YES | NO | N/A
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| HORIZ. COPPER | HORIZONTAL CABLE MFG | ANY | ANY | COMMSCOPE | PANDUIT / GENERAL | BERKTEK | ICC | OTHER
|  | HORIZONTAL CONNECTIVITY | ANY | ANY | COMMSCOPE | PANDUIT | LEVITON | ICC | OTHER
|  | CATEGORY | CATEGORY 6 OR BETTER | CATEGORY 6 OR BETTER | CATEGORY 3 | CATEGORY 5 / 5E | CATEGORY 6/6E | CATEGORY 6A | COMBINATION
MED |  | SPARE PORTS ON PANEL | AVAILABLE | AVAILABLE | AVAILABLE | AT CAPACITY

## CRITICAL SERVER ROOM
PRIORITY |  |  | LEGACY MINIMUM | UHS IT STANDARD
| GENERAL | DATE / TIME |  |  | DATE AND TIME
|  | INSPECTOR NAME |  |  | #
|  | CAMPUS |  |  | CLEAR LAKE | DOWNTOWN | MAIN | VICTORIA
|  | BUILDING |  |  | TEXT
|  | ROOM NUMBER |  |  | TEXT
HIGH |  | TEMPERATURE | 60 - 75F | 60 - 75F | #
HIGH |  | HUMIDITY | 30 - 50% RH | 30 - 50% RH | #
HIGH |  | ASSET TAG ON DOOR FRAME | YES | YES | # | NONE
HIGH |  | CONTROLLABLE THERMOSTAT | YES | YES | YES | NOT CONTROLLABLE | NONE IN ROOM
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | ROOM INFORMATION | ROOM TYPE | SHARED MOSTLY IT | DEDICATED | DEDICATED | SHARED MOSTLY IT | SHARED MOSTLY OTHERS
HIGH |  | ACCESS | READER W/ IT MASTER KEY | READER W/ IT MASTER KEY | CARD READER | IT MASTER KEYED | COMMON KEYED | NONE
HIGH |  | CAMERA INTERIOR | YES | YES | YES | NO |  | NON OPERATIONAL
CS |  | CAMERA EXTERIOR | YES OR NOT REQUIRED | YES OR NOT REQUIRED | YES | NO | NOT REQUIRED | NON OPERATIONAL
HIGH |  | DOOR TYPE | SOLID | SOLID | SOLID | LOUVERED | GLASS
MED |  | ROOM LABEL | YES | YES | YES | NO
MED |  | DOOR SWING | DOES NOT AFFECT ROOM USE | OUT | OUT | IN | AFFECTS ROOM USE
HIGH |  | LIGHTING | OPERATIONAL | SWITCH | SWITCH | MOTION | NONE | SWITCH NON OPERATIONAL | MOTION NON OPERATIONAL
HIGH |  | WALLS TO DECK | YES | YES | YES | NO
LOW |  | CEILING | ANY | OPEN/NONE | OPEN/NONE | SHEETROCK | CEILING TILE
HIGH |  | FIRE SUPPRESSION | CLEAN AGENT | CLEAN AGENT | BUILDING STANDARD | PRE-ACTION | CLEAN AGENT | NONE (EXTIGUISHER REQ)
LOW |  | SPRINKLER HEADS | CAGED | CAGED | CAGED | NOT CAGED | NONE
HIGH |  | INSPECTED FIRE EXTINGUISHER | IF NO FIRE SUPPRESSION | NOT REQUIRED | NOT REQUIRED | CO2 OR CLEAN AGENT | WET TYPE (REPLACE) | INSPECTION REQUIRED
HIGH |  | SPACE FOR GROWTH | YES | YES | YES | NO
HIGH |  | ROOM SIGN-IN SHEET AVAILABLE | YES | YES | YES | NO
MED |  | EQUIP. STORAGE / UNBOXING SPACE | NOT SERVER ROOM BEING USED | ADJACENT TO ROOM | ADJACENT TO ROOM | IN BUILDING | SERVER ROOM BEING USED | IN SEPARATE BUILDING | NONE
MED |  | STAFF OFFICE SPACE | NOT SERVER ROOM BEING USED | ADJACENT TO ROOM | ADJACENT TO ROOM | IN BUILDING | SERVER ROOM BEING USED | IN SEPARATE BUILDING | NONE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | HOUSE KEEPING | TRASH IN ROOM | NO | NO | NO | YES, REMOVE
LOW |  | FLOOR IS CLEAN | YES | YES | NO | YES, CLEANING REQUIRED
MED |  | EQUIPMENT DUST FREE | YES | YES | NO | YES, CHECK ROOM PRESSURE
MED |  | INAPROPRIATE STORAGE | NO | NO | NO | YES
MED |  | RAISED FLOOR IS CONJESTED | NO | NO | NO / NA | YES, REWORK IS REQUIRED
HIGH |  | ABANDONED CABLING | NO | NO | NO | YES
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | NON SERVICING SYSTEMS | WATER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | SEWER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | FIRE MAIN | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ROOF DRAINS | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
MED |  | ELECTRICAL PANELS | NO OR SERVICES ROOM | NO | NO | YES, SERVICES ROOM | YES, NOT APPROVED BY IT
MED |  | ACCESS CONTROL PANELS | NO OR IF APPROVED BY IT | NO OR IF APPROVED BY IT | NO | YES, APPROVED BY IT | YES, NOT APPROVED BY IT
MED |  | AV SYSTEMS | NO OR YES, APPROVED BY IT | NO OR IF APPROVED BY IT | NO | YES, APPROVED BY IT | YES, NOT APPROVED BY IT
|  |  | LEGACY MINIMUM | UHS IT STANDARD
MED | ROOM CABLE SUPPORT | OVERHEAD CABLE SUPPORT | ANY (NOT NONE) | BASKET OR LADDER | BASKET | LADDER | HOOKS | NONE, SUPPORT REQUIRED
MED |  | WALL CABLE SUPPORT | ANY (NOT NONE) | LADDER | BASKET | LADDER | D-RINGS | NONE, SUPPORT REQUIRED
MED |  | SUPPORT CAPACITY | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | TRAY FULL | REWORK REQUIRED
LOW |  | CABLE TRAY DRESSING | NEAT AND TIDY | NEAT AND TIDY | NEAT AND TIDY | REDRESSING REQUIRED
HIGH |  | HORIZONTAL PENETRATIONS | COMPLIANT OR SEALED | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | HORZ. PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | VERTICAL PENETRATIONS | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | NOT APPLICABLE
MED |  | VERTL PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | INCOMMING OSP CONDUIT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | OSP CONDUIT SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
MED |  | RAISED FLOOR | YES OR NONE | YES OR NONE | NO | YES, IN GOOD CONDITION | YES, MISSING TILES
MED |  | UNDER FLOOR CAPACITY | SPARE CAPACITY OR NA | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
MED |  | FIBER RUNNER | YES OR NOT REQUIRED | YES | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | MEP | LIGHTS | EMERGENCY | EMERGENCY | EMERGENCY | HOUSE POWER | NOT SUFFICIENT | UNKNOWN SUFFICIENT
HIGH |  | HVAC | DEDICATED | DEDICATED | DEDICATED | BUILDING AIR | NONE | UNKNOWN
|  | HVAC TYPE | ANY | ANY | CHILLED WATER | DX | BOTH | UNKNOWN
HIGH |  | HVAC N+1 | YES OR SERVICE W/OUT INTERUPTION | YES | YES | NO | SERVICE W/OUT INTERUPTION
|  | HVAC SUPPLY | ANY | ANY | UNDERFLOOR | DUCTED | INLINE | OTHER
|  | HVAC RETURN | ANY | ANY | DUCTED | PLENUM / VIA CEILING | INLINE | OTHER
|  | GENERATOR TYPE | ANY | ANY | DIESEL | NATURAL GAS | PROPANE | MULTI-FUEL
HIGH |  | GENERATOR N+1 | YES OR SERVICE W/OUT INTERUPTION | YES | YES | NO | SERVICE W/OUT INTERUPTION
HIGH |  | POWER FEED TO UPS | DUAL | DUAL | SINGLE | DUAL | OTHER
HIGH |  | POWER FEED TO CABINETS | DUAL UPS/UPS | DUAL UPS / UPS | SINGLE UPS | SINGLE HOUSE POWER | DUAL UPS/HOUSE | DUAL UPS/UPS
HIGH |  | CONVENIENCE POWER | EMERGENCY OR HOUSE POWER | EMERGENCY | EMERGENCY | HOUSE POWER | NONE | INSUFFICIENT
MED |  | HVAC TEMPERATURE MONITORING | ANY | EACH ROW HOT & COLD | ONE LOCATION | MULTIPLE LOCATIONS | EACH ROW | EACH ROW HOT & COLD
MED |  | CABINET TEMPERATURE MONITORING | ANY EXCEPT NONE | ALL CABINETS | ALL CABINETS | SELECT CABINETS | NONE | VIA SERVER
MED |  | PDU LOAD MONITORING | ANY | YES | YES | NO
LOW |  | NOISE LEVEL (DB) | UNDER 95dB | UNDER 95dB | #
MED |  | POSITIVE ROOM PRESSURE | YES | YES | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | GROUNDING AND BONDING | BUSS BAR | YES | YES | YES | NO
HIGH |  | TWO HOLE TUGS USED | YES | YES | YES | NO
HIGH |  | TRAY BONDED TO TGB | YES | YES | YES | NO
HIGH |  | RACK/CABINET BONDED | TO BUSS BAR OR UNDERFLOOR CONDUCTORS | TO BUSS BAR OR UNDERFLOOR CONDUCTORS | TO BUSS BAR | TO UNDERFLOOR CONDUCTORS | NOT BONDED
HIGH |  | UPS BONDED | TO BUSS BAR OR UNDERFLOOR CONDUCTORS | TO BUSS BAR OR UNDERFLOOR CONDUCTORS | TO BUSS BAR | TO UNDERFLOOR CONDUCTORS | NOT BONDED
HIGH |  | PDU(S) BONDED TO CABINET | YES | YES | YES | NO | NA
HIGH |  | OSP CABLE EQUIPMENT | YES | YES | YES | NO | NA
HIGH |  | RAISED FLOOR | YES | YES | YES | NO | NA
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| RACK RELATED | CABINETS ARE SECURE FRONT & BACK | READER OR UNIQUE LOCKS FRONT & BACK | READER OR UNIQUE LOCKS FRONT & BACK | ACCESS CONTROLLED | LOCKED FRONT AND BACK | UNIQUE LOCKS FRONT & BACK
|  | NUMBER OF CABINETS |  |  | #
MED |  | CABINETS INVENTORY IS CURRENT | YES | YES | YES | NO | REQUIRES UPDATE
MED |  | COLOCATION CABINETS IN SPACE | YES, SECURITY SPACE OR ESCORT REQUIRED | YES, SECURE SPACE | YES, SECURE SPACE | YES, ESCORT REQUIRED | NONE
MED |  | UNIQUE SECURITY FOR COLO CABINETS |  | YES, ALL CABINETS UNIQUE | YES | FROM IT CABINETS ONLY | SAME KEYS AT IT CABINETS
LOW |  | SPARE PATCH PANEL PORTS | 6 OR MORE | 6 OR MORE | # | #
LOW |  | VERTICAL MANAGERS | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | REDRESSING REQUIRED | FULL | NONE
LOW |  | HORIZONTAL MANAGERS | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | REDRESSING REQUIRED | FULL | NONE
HIGH |  | FRONT CLEARANCE | NOT UNSAFE | 3FT+ | 3FT+ | 2FT+ | NONE | UNSAFE
HIGH |  | REAR CLEARANCE | NOT UNSAFE | 3FT+ | 3FT+ | 2FT+ | NONE | UNSAFE
LOW |  | ROOM FOR ADD'L RACK/CABINET | YES OR EMPTY RACKS AVAILABLE | YES OR EMPTY RACKS AVAILABLE | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| UPS | UPS TYPE | IN CABINET OR CENTRALIZED | CENTRALIZED | IN CABINET | CENTRALIZED | NONE
HIGH |  | UPS STATUS | PASSED TEST | PASSED TEST | PASSED TEST | FAILS TEST | NONE
HIGH |  | UPS MONITORED | YES | YES | YES | NO
MED |  | ROOM TEMP MONITORING | YES | YES | YES | NO | YES, BUT NOT VIA UPS
MED |  | SPARE CAPACITY | YES | YES | YES | NO | NA
US |  | STEP DOWN TRANSFORMER | ANY | ANY | YES | NO | NA
HIGH |  | UPS N+1 | YES OR SERVICE W/OUT INTERUPTION | YES | YES | NO | SERVICE W/OUT INTERUPTION
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | LABELING | ROOM | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | RACKS/CABINETS | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | FIBER CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | FIBER PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BACKBONE COPPER CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BACKBONE COPPER PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | HORIZONTAL CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | HORIZONTAL PATCH PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | SWITCHES | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | UPS | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BUSS BAR | YES | YES | YES | NO | UPDATE REQUIRED
HIGH |  | FIRE STOP ASSEMBLIES | YES | YES | YES | NO | UPDATE REQUIRED
MED |  | SERVERS AND OTHER APPLIANCES | YES | YES | YES | NO | UPDATE REQUIRED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| BACK BONE | FIBER CABLE MFG | ANY | ANY | COMMSCOPE | CORNING | PYRSMIAN | DRAKA | OTHER
|  | FIBER CONNECTIVITY | ANY | ANY | LC | ST | APC | SC | COMBINATION
MED |  | FIBER AT CAPACITY | NO | NO | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| HORIZ. COPPER | HORIZONTAL CABLE MFG | BUILDING SPECIFIC | BUILDING SPECIFIC | COMMSCOPE | PANDUIT / GENERAL | BERKTEK | ICC | OTHER
|  | HORIZONTAL CONNECTIVITY | BUILDING SPECIFIC | BUILDING SPECIFIC | COMMSCOPE | PANDUIT | LEVITON | ICC | OTHER
|  | CATEGORY | CATEGORY 6 OR BETTER | CATEGORY 6 OR BETTER | CATEGORY 3 | CATEGORY 5 / 5E | CATEGORY 6/6E | CATEGORY 6A | COMBINATION
MED |  | SPARE PORTS ON PANEL/SWITCH | AVAILABLE | AVAILABLE | AVAILABLE | AT CAPACITY

## DATA CENTER
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| GENERAL | DATE / TIME |  |  | DATE AND TIME
|  | INSPECTOR NAME |  |  | #
|  | CAMPUS |  |  | CLEAR LAKE | DOWNTOWN | MAIN | VICTORIA
|  | BUILDING |  |  | TEXT
|  | ROOM NUMBER |  |  | TEXT
HIGH |  | TEMPERATURE | 60 - 75F | 60 - 75F | #
HIGH |  | HUMIDITY | 30 - 50% RH | 30 - 50% RH | #
HIGH |  | ASSET TAG ON DOOR FRAME | YES | YES | # | NONE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | ROOM INFORMATION | ROOM TYPE | SHARED MOSTLY IT | DEDICATED | DEDICATED | SHARED MOSTLY IT | SHARED MOSTLY OTHERS
HIGH |  | ACCESS | READER W/ IT MASTER KEY | READER W/ IT MASTER KEY | CARD READER | IT MASTER KEYED | COMMON KEYED | NONE
HIGH |  | CAMERA INTERIOR | YES | YES | YES | NO |  | NON OPERATIONAL
CS |  | CAMERA EXTERIOR | YES OR NOT REQUIRED | YES OR NOT REQUIRED | YES | NO | NOT REQUIRED | NON OPERATIONAL
HIGH |  | DOOR TYPE | SOLID | SOLID | SOLID | LOUVERED | GLASS
MED |  | ROOM LABEL | YES | YES | YES | NO
MED |  | DOOR SWING | DOES NOT AFFECT ROOM USE | OUT | OUT | IN | AFFECTS ROOM USE
HIGH |  | LIGHTING | OPERATIONAL | SWITCH | SWITCH | MOTION | NONE | SWITCH NON OPERATIONAL | MOTION NON OPERATIONAL
HIGH |  | WALLS TO DECK | YES | YES | YES | NO
LOW |  | CEILING | ANY | OPEN/NONE | OPEN/NONE | SHEETROCK | CEILING TILE
HIGH |  | FIRE SUPPRESSION | CLEAN AGENT | CLEAN AGENT | BUILDING STANDARD | PRE-ACTION | CLEAN AGENT | NONE (EXTIGUISHER REQ)
LOW |  | SPRINKLER HEADS | CAGED | CAGED | CAGED | NOT CAGED | NONE
HIGH |  | INSPECTED FIRE SYSTEM | IF NO FIRE SUPPRESSION | NOT REQUIRED | NOT REQUIRED | CURRENT | INSPECTION REQUIRED | WET SPRINKLER (REPLACE)
HIGH |  | SPACE FOR GROWTH | YES | YES | YES | NO
HIGH |  | ROOM SIGN-IN SHEET REQUIRED | YES | YES | YES | NO
MED |  | EQUIP. STORAGE / UNBOXING SPACE | NOT SERVER ROOM BEING USED | ADJACENT TO ROOM | ADJACENT TO ROOM | IN BUILDING | SERVER ROOM BEING USED | IN SEPARATE BUILDING | NONE
MED |  | STAFF OFFICE SPACE | NOT SERVER ROOM BEING USED | ADJACENT TO ROOM | ADJACENT TO ROOM | IN BUILDING | SERVER ROOM BEING USED | IN SEPARATE BUILDING | NONE
|  | FLOOR TYPE | ANY | RAISED FLOOR | RAISED FLOOR | SEALED CONCRETE | VINYL TILE
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | HOUSE KEEPING | TRASH IN ROOM | NO | NO | NO | YES, REMOVE
LOW |  | FLOOR IS CLEAN, WHOLE & SAFE | YES | YES | YES | NO, CLEANING REQUIRED | TILES ARE MISSING
MED |  | EQUIPMENT DUST FREE | YES | YES | YES | NO, CHECK ROOM PRESSURE
MED |  | INAPROPRIATE STORAGE | NO | NO | NO | YES, REMOVE
MED |  | RAISED FLOOR IS CONJESTED | NO | NO | NO / NA | YES, REWORK IS REQUIRED
HIGH |  | ABANDONED CABLING | NO | NO | NO | YES
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | NON SERVICING SYSTEMS | WATER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | SEWER PIPES | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | FIRE MAIN | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ROOF DRAINS | NO OR DRIP PAN INSTALLED | NO | NO | YES, DRIP PAN INSTALLED | YES, DRIP PAN NEEDED
HIGH |  | ELECTRICAL PANELS | NO OR SERVICES ROOM | NO | NO | YES, SERVICES ROOM | YES, NOT APPROVED BY IT
HIGH US |  | ACCESS CONTROL PANELS | NO OR IF APPROVED BY IT | NO OR IF APPROVED BY IT | NO | YES, APPROVED BY IT | YES, NOT APPROVED BY IT
HIGH US |  | AV SYSTEMS | NO OR YES, APPROVED BY IT | NO OR IF APPROVED BY IT | NO | YES, APPROVED BY IT | YES, NOT APPROVED BY IT
|  |  | LEGACY MINIMUM | UHS IT STANDARD
MED | ROOM CABLE SUPPORT | OVERHEAD CABLE SUPPORT | ANY (NOT NONE) | BASKET OR LADDER | BASKET | LADDER | HOOKS | NONE, SUPPORT REQUIRED
MED |  | WALL CABLE SUPPORT | ANY (NOT NONE) | LADDER | BASKET | LADDER | D-RINGS | NONE, SUPPORT REQUIRED
MED |  | SUPPORT CAPACITY | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | TRAY FULL | REWORK REQUIRED
LOW |  | CABLE TRAY DRESSING | NEAT AND TIDY | NEAT AND TIDY | NEAT AND TIDY | REDRESSING REQUIRED
HIGH |  | HORIZONTAL PENETRATIONS | COMPLIANT OR SEALED | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | HORZ. PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | VERTICAL PENETRATIONS | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | NOT APPLICABLE
MED |  | VERTL PENETRATION SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
HIGH |  | INCOMMING OSP CONDUIT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP COMPLIANT | FIRE-STOP NON COMPLIANT | PENETRATIONS SEALED | PENETRATIONS NOT SEALED
MED |  | OSP CONDUIT SPACE | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED
MED |  | RAISED FLOOR | YES OR NONE | YES OR NONE | NONE | YES, IN GOOD CONDITION | YES, MISSING TILES
MED |  | UNDER FLOOR CAPACITY | SPARE CAPACITY OR NA | SPARE CAPACITY | SPARE CAPACITY | FULL | OVERFILLED | NA
MED |  | FIBER RUNNER | YES OR NOT REQUIRED | YES | YES | NOT REQUIRED | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | MEP | LIGHTS | EMERGENCY | EMERGENCY | EMERGENCY | HOUSE POWER | NOT SUFFICIENT | UNKNOWN SUFFICIENT
HIGH |  | HVAC | DEDICATED | DEDICATED | DEDICATED | BUILDING AIR | NONE | UNKNOWN
|  | HVAC TYPE | ANY | ANY | CHILLED WATER | DX | BOTH | UNKNOWN
HIGH |  | HVAC N+1 | YES OR SERVICE W/OUT INTERUPTION | YES | YES | NO | SERVICE W/OUT INTERUPTION
|  | HVAC SUPPLY | ANY | ANY | UNDERFLOOR | DUCTED (COLD AISLE) | INLINE | OTHER
|  | HVAC RETURN | ANY | ANY | DUCTED (HOT AISLE) | PLENUM / VIA CEILING | INLINE | OTHER
|  | GENERATOR TYPE | ANY | ANY | DIESEL | NATURAL GAS | PROPANE | MULTI-FUEL
HIGH |  | GENERATOR N+1 | YES OR SERVICE W/OUT INTERUPTION | YES | YES | NO | SERVICE W/OUT INTERUPTION
HIGH |  | CABINET POWER OUTLETS | ANY LOCKING | OVER CABINET LOCKING | OVER CABINET LOCKING | OVER CABINET NOT LOCKING | UNDER CABINET LOCKING | UNDER CABINET NOT LOCKING
HIGH |  | POWER FEED TO UPS | DUAL | DUAL | SINGLE | DUAL | OTHER
HIGH |  | POWER FEED TO CABINETS | DUAL UPS/UPS | DUAL UPS / UPS | SINGLE UPS | SINGLE HOUSE POWER | DUAL UPS/HOUSE | DUAL UPS/UPS
MED |  | CONVENIENCE POWER | EMERGENCY OR HOUSE POWER | EMERGENCY | EMERGENCY | HOUSE POWER | NONE | INSUFFICIENT
MED |  | HVAC TEMPERATURE MONITORING | ANY | EACH ROW HOT & COLD | ONE LOCATION | MULTIPLE LOCATIONS | EACH ROW | EACH ROW HOT & COLD
MED |  | CABINET TEMPERATURE MONITORING | ANY EXCEPT NONE | ALL CABINETS | ALL CABINETS | SELECT CABINETS | NONE | VIA SERVER
LOW |  | PDU LOAD MONITORING | ANY | YES | YES | NO
MED |  | NOISE LEVEL (DB) | UNDER 95dB | UNDER 95dB | #
HIGH |  | POSITIVE ROOM PRESSURE | YES | YES | YES | NO
HIGH |  | LEAK DETECTION | YES | YES | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
HIGH | GROUNDING AND BONDING | BUSS BAR | YES | YES | YES | NO
HIGH |  | TWO HOLE TUGS USED | YES | YES | YES | NO
HIGH |  | TRAY BONDED TO TGB | YES | YES | YES | NO
HIGH |  | RACK/CABINET BONDED | TO BUSS BAR OR UNDERFLOOR CONDUCTORS | TO BUSS BAR OR UNDERFLOOR CONDUCTORS | TO BUSS BAR | TO UNDERFLOOR CONDUCTORS | NOT BONDED
HIGH |  | UPS BONDED | TO BUSS BAR OR UNDERFLOOR CONDUCTORS | TO BUSS BAR OR UNDERFLOOR CONDUCTORS | TO BUSS BAR | TO UNDERFLOOR CONDUCTORS | NOT BONDED
HIGH |  | PDU(S) BONDED TO CABINET | YES | YES | YES | NO | NA
HIGH |  | OSP CABLE EQUIPMENT | YES | YES | YES | NO | NA
HIGH |  | RAISED FLOOR | YES | YES | YES | NO | NA
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| RACK RELATED | CABINETS ARE SECURE FRONT & BACK | READER OR UNIQUE LOCKS FRONT & BACK | READER OR UNIQUE LOCKS FRONT & BACK | READER | SAME LOCKED FRONT AND BACK | UNIQUE LOCKS FRONT & BACK
|  | NUMBER OF CABINETS |  |  | #
MED |  | CABINETS INVENTORY IS CURRENT | YES | YES | YES | NO | REQUIRES UPDATE
MED |  | COLOCATION CABINETS IN SPACE | YES, SECURITY SPACE OR ESCORT REQUIRED | YES, SECURE SPACE | YES, SECURE SPACE | YES, ESCORT REQUIRED | NONE
MED |  | UNIQUE SECURITY FOR COLO CABINETS |  | YES, ALL CABINETS UNIQUE | YES, ALL CABINETS UNIQUE | UNIQUE FROM IT CABINETS | SAME KEYS AS IT CABINETS | NO SECURITY ON COLO CABINETS
LOW |  | SPARE PATCH PANEL PORTS | 6 OR MORE | 6 OR MORE | # | #
LOW |  | VERTICAL MANAGERS | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | REDRESSING REQUIRED | FULL | NONE
LOW |  | HORIZONTAL MANAGERS | SPARE CAPACITY | SPARE CAPACITY | SPARE CAPACITY | REDRESSING REQUIRED | FULL | NONE
HIGH |  | FRONT CLEARANCE | NOT UNSAFE | 3FT+ | 3FT+ | 2FT+ | 4FT+ | UNSAFE
HIGH |  | REAR CLEARANCE | NOT UNSAFE | 3FT+ | 3FT+ | 2FT+ | 4FT+ | UNSAFE
LOW |  | ROOM FOR ADD'L RACK/CABINET | YES OR EMPTY RACKS AVAILABLE | YES OR EMPTY RACKS AVAILABLE | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| UPS | UPS TYPE | IN CABINET OR CENTRALIZED | CENTRALIZED | IN CABINET | CENTRALIZED | NONE
HIGH |  | UPS STATUS | PASSED TEST | PASSED TEST | PASSED TEST | FAILS TEST | NONE
HIGH |  | UPS MONITORED | YES | YES | YES | NO
MED |  | ROOM TEMP MONITORING | YES | YES | YES | NO | YES, BUT NOT VIA UPS
MED |  | SPARE CAPACITY | YES | YES | YES | NO | NA
US |  | STEP DOWN TRANSFORMER | ANY | N/A | YES | NO | NA
HIGH |  | UPS N+1 | YES OR SERVICE W/OUT INTERUPTION | YES | YES | NO | SERVICE W/OUT INTERUPTION
|  |  | LEGACY MINIMUM | UHS IT STANDARD
LOW | LABELING | ROOM | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | RACKS/CABINETS | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | FIBER CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | FIBER PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BACKBONE COPPER CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BACKBONE COPPER PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | HORIZONTAL CABLE | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | HORIZONTAL PATCH PANEL | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | SWITCHES | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | UPS | YES | YES | YES | NO | UPDATE REQUIRED
LOW |  | BUSS BAR | YES | YES | YES | NO | UPDATE REQUIRED
HIGH |  | FIRE STOP ASSEMBLIES | YES | YES | YES | NO | UPDATE REQUIRED
MED |  | SERVERS AND OTHER APPLIANCES | YES | YES | YES | NO | UPDATE REQUIRED
MED |  | COLOCATION SPACES & CABINETS | YES | YES | YES | NO | UPDATE REQUIRED
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| BACK BONE | FIBER CABLE MFG | ANY | ANY | COMMSCOPE | CORNING | PYRSMIAN | DRAKA | OTHER
|  | FIBER CONNECTIVITY | ANY | ANY | LC | ST | APC | SC | COMBINATION
MED |  | FIBER AT CAPACITY | NO | NO | YES | NO
|  |  | LEGACY MINIMUM | UHS IT STANDARD
| HORIZ. COPPER | HORIZONTAL CABLE MFG | ANY | ANY | COMMSCOPE | PANDUIT / GENERAL | BERKTEK | ICC | OTHER
|  | HORIZONTAL CONNECTIVITY | ANY | ANY | COMMSCOPE | PANDUIT | LEVITON | ICC | OTHER
|  | CATEGORY | CATEGORY 6 OR BETTER | CATEGORY 6 OR BETTER | CATEGORY 3 | CATEGORY 5 / 5E | CATEGORY 6/6E | CATEGORY 6A | COMBINATION
MED |  | SPARE PORTS ON PANEL/SWITCH | AVAILABLE | AVAILABLE | AVAILABLE | AT CAPACITY